## Sheet1
Intro | [10 empty] | Task | [6 empty] | Primary Fail | [8 empty] | Criticality and Task Assess | [9 empty] | Examination | [8 empty] | Protective Fail |  |  |  |  | Strategy Added
TMC code | Category | Equipment | TMC | Band | Function | Functional Failure | Failure Cause | No. | Local Effect | System Effect | Proposed Task | Test | Scheduled Task | Decision Basis | Corrective Task | Scheduled Interval | Packaged Notes | Operation Loss: | Operation Loss: | Cond Fail: | Funct Fail: | Total Fail: | Pop'n: | CF Interval | MTBF | MTBF basis | Evident Failure | Safety Impact | Environment Impact | Operation Impact | Lube/Service | On Condition | Restoration | Discard | Failure Finding | Redesign | Exam Crew | Examination Time (m): | Exam Success | Setup Cost | Exam Cost | Planned Repair Cost | Call Out, Secondary Damage | Unplanned Failure Cost | Optimal Interval | Protective systems | Protective Population | Protective MTBF | Protective Repair | Protective Failures | Asset Consequence Model | Level Consequence Model | Notes
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING damaged porcelain due to flashover due to lightning. (Normal operation). | 2 | Flashover, | possible secondary damage and flying porcelain. Loss of supply from transformer. | Examine all transformer bushing surfaces for damage. |  | Examine all transformer bushing surfaces for damage. |  | TX bushing clean / repair. # TX bushing replace. | ZS Inspect |  | 0 | N/A | 1.09 | 0.18 | 1.27 | 590 | 0 | 169567 | See code 110 | Y | Y | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING damaged porcelain due to vandalism. (Normal operation). | 3 | Flashover, | possible secondary damage and flying porcelain. Loss of supply from transformer. | Examine all transformer bushing surfaces for damage. |  | Examine all transformer bushing surfaces for damage. | Package a task in the substation zonal inspection ? | TX bushing clean / repair. # TX bushing replace. | ZS Inspect |  | 0 | N/A | 0 | 0.18 | 0.18 | 590 | 0 | 1196389 | see code 110 for data | Y | Y | N | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 01) Transformation of power from primary to secondary voltage within assigned rating. | a) Does not transform power from primary to secondary voltage. | BUSHINGS faulty connection due to corrosion / poor connection. (Normal operation). | 4 | Overheated Connection | Possible loss of supply | Examine bushing connection condition on load using infrared camera. |  | Examine bushing connection condition on load using infrared camera. | Assumes whole zone thermovision and 30 items of equipment across $330 setup. | TX bushing connection clean / repair. | Infrared Scan |  | 120000 | Min Impact / Med Equipment Damage | 7.7 | 0.55 | 8.25 | 770 | 1460 | 34067 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | Y |  |  |  |  | Substation Crew | 10 | 95 | 15 | 0 | 2500 | 142500 | 20000 | 631 | 1 | 0 | 0 | 0 | 0 |  |  | hot joint bushing
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING internal fault due to oil loss. (Normal operation). | 5 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | Check bushing sight glass for correct oil level. |  | Check bushing sight glass for correct oil level. |  | TX bushing clean / repair. | ZS Inspect |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | Y | N | Y | Y | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING low resistance due to surface contamination. (Normal operation). | 6 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | Examine transformer bushing surface for contamination. |  | Examine transformer bushing surface for contamination. | Completed as part of diagonistic maintenance | TX bushing clean / repair. | 6yr Maint. |  | 12000 | Min Impact / Min Equipment Damage |  | 0 |  |  | 0 | 0 |  | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 |  |  | 0 | 0 | 12000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | WINDING insulation failure due to ingress of moisture. (Normal operation). | 7 | Possible shorted turns, damage to transformer. | To be updated | Test transformer oil for water content is less than (30ppm) and record oil temperature. | Oil Sample | Test the transformer oil sample from main tank valve for water content less than 30ppm and record oil temperature. | Temp. recorded accurately at time of sampling to be used to for paper condition monitoring. | TX oil replacement with filtered oil. # TX replace. | 3yr Moisture Sample |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | RADIATOR ineffective cooling due to fin blocked. (Normal operation). | 10 | Overheating alarm, reduction in transformer life.. | To be updated | N.S.M. |  | N.S.M. |  | TX radiator repair. | N.S.M. |  | 50000 | Network disruption (30 min) | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | OIL loss of insulation due to low electric strength (breakdown kV). (Normal operation). | 12 | Possible failure of transformer. | To be updated | Test transformer oil sample electric strength is greater than 25kV (For transformers of nominal 33kV and below), 35kV (for transformers above 33kV) | Oil Sample | Test the transformer oil sample from main tank valve for inhibitor level, electric strength, acidity, interfacial tension and estimated degree of polymerisation. | Test more frequently once oil has failed an test parameter. | TX oil replacement with filtered oil. # TX oil sample required. | 6yr Full Oil Sample |  | 120000 | Min Impact / Med Equipment Damage | 1.45 | 0.1 | 0 | 770 | 3650 | 181323 | CF is an estimate on how long we have left them after failing this test.. Original MRA Ccf:100; Ccf:0.1; Pop:500; MTBF:1823.177; Cfint:3650; OptimumInt: 0 | N | Y | Y | Y | N | N | N | N | Y |  | Substation Crew (2) | 10 | 90 | 55 | 91.67 | 60000 | 980000 | 800000 | 538 | 1 | 211 | 32090 | 60000 | 2.4 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | OIL loss of insulation due to poor oil quality. (Normal operation). | 17 | Possible failure of transformer. | To be updated | Test the transformer oil sample from main tank valve for inhibitor level, electric strength, acidity, interfacial tension and estimated degree of polymerisation. | Oil Sample | Test the transformer oil sample from main tank valve for inhibitor level, electric strength, acidity, interfacial tension and estimated degree of polymerisation. | Examination costs correct primary fail to be filled at later date. $55 per includes travel, | TX oil replacement with filtered oil. # TX oil sample required. | 6yr Full Oil Sample |  | 120000 | Min Impact / Med Equipment Damage | 6.6 | 0.1 | 0 | 770 | 3650 | 41948 | Get oil data at later date to tighten dates up | N | Y | Y | Y | N | N | N | N | Y |  | Substation Crew (2) | 15 | 98 | 55 | 110 | 40000 | 960000 | 800000 | 268 | 1 | 210 | 11614 | 40000 | 6.6 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | OIL loss of insulation due to moisture contamination. (Normal operation). | 19 | Possible failure of transformer. | To be updated | Test transformer oil for water content less than (30ppm) and record oil temperature. | Oil Sample | Test the transformer oil sample from main tank valve for water content less than 30ppm and record oil temperature. | Temp. recorded accurately at time of sampling to be used to for paper condition monitoring. | TX oil replacement with filtered oil. # TX oil sample required. | 3yr Moisture Sample |  | 120000 | Min Impact / Med Equipment Damage | 0 | 0.1 | 0 | 770 | 0 | 2810500 | See Contaminated oil above.. Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 2487.494 | N | N | N | Y | N | N | N | N | Y |  | Substation Crew (2) | 20 | 95 | 55 | 128.33 | 60000 | 980000 | 800000 | 806 | 1 | 782.2 | 4067 | 60000 | 70.2 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | OIL contaminated due to rusty / wet conservator. (Normal operation). | 20 | Possible damage to transformer. | To be updated | N.S.M. |  | N.S.M. |  | TX conservator repair. | N.S.M. |  | 0 | N/A | 23 | 0 | 0 | 770 | 0 | 12220 | Original MRA Ccf:40; Ccf:0; Pop:500; MTBF:4562.5; Cfint:7200; OptimumInt: 3250.189 | N | N | N | Y | N | N | N | N | N | N |  | 15 | 98 | 500 | 0 | 5000 | 505000 | 500000 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | tank damage
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | TX BREATHER moisture ingress due to silica gel consumed. (Normal operation). | 21 | Possible ingress of moisture transformer transformer. | To be updated | Examine silica gel in dehydrating breather for at least 50% blue colour. |  | Examine silica gel for at least 50% blue colour. | Hard time replacements not viable due to variation in TX environments and condition. Crews carry containers of Silica Gel in their vehicle and can replace on condition. | TX silica gel replace. | ZS Inspect |  | 0 | N/A | 15.45 | 0.36 | 15.81 | 590 | 500 | 13621 | Original MRA Ccf:400; Ccf:50; Pop:500; MTBF:405.5555; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 75 | 40 | 58.33 | 200 | 1200 | 1000 | -5076.3647 | 1 | 0 | 0 | 0 | 0 |  |  | breather failure
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | TX BREATHER moisture ingress due to cracked or broken cylinder. (Normal operation). | 22 | Possible ingress of moisture transformer transformer. | To be updated | N.S.M. |  | N.S.M. | Corrective task. | TX silica gel cylinder repair / replace. | N.S.M. |  | 0 | N/A | 4.36 | 4.36 | 8.72 | 590 | 0 | 24696 | No CF . Original MRA Ccf:0; Ccf:15; Pop:500; MTBF:12166.67; Cfint:0; OptimumInt: 3250.189 | N | N | N | N | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | breather failure
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to deteriorated gaskets. (Normal operation). | 23 | Possible damage to transformer. | To be updated | Examine transformer for signs of external oil leaks and check oil level. |  | Examine all of transformer for signs of external oil leaks and check conservator oil level. | Replace gasket if oil leak is greater than 200 ltres per year | TX oil leak repair. | ZS Inspect |  | 0 | N/A | 47.64 | 0.01 | 47.65 | 590 | 2190 | 4519 | Original MRA Ccf:19; Ccf:0.01; Pop:500; MTBF:9600.21; Cfint:2190; OptimumInt: 388.4354 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 10 | 50 | 20 | 0 | 20000 | 20760 | 760 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to corrosion. (Normal operation). | 24 | Possible damage to transformer. | To be updated | Examine transformer exterior for signs of excessive corrosion. |  | Examine transformer exterior for signs of excessive corrosion. | Repaint of transformer should be considered as an on condition task.(JB - 18 years - justification?) | TX corrosion treatment (paint). | ZS Inspect |  | 120000 | Min Impact / Med Equipment Damage | 40 | 0 | 40 | 770 | 14400 | 7026 |  | N | Y | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 15 | 75 | 20 | 0 | 6000 | 626000 | 500000 | 2049 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to leaking gauge glass. (Normal operation). | 25 | Possible damage to transformer transformer protection devices. | To be updated | Examine gauge glass for signs of oil leaks. |  | Examine gauge glass for signs of oil leaks. | To replace leaking gauge glass, drop oil level below gauge glass, remove glass & gasket, clean all surfaces with methylated spirits, paint white backing, manufacture new gasket, replace parts when paint is dry, refill with oil. Check for leaks, caution t | TX oil leak repair. | ZS Inspect |  | 0 | N/A | 10 | 0.01 | 10.01 | 500 | 2190 | 18232 | Original MRA Ccf:10; Ccf:0.01; Pop:500; MTBF:18231.77; Cfint:2190; OptimumInt: 1341.83 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 95 | 20 | 0 | 3000 | 3000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to leaking cocks (valves). (Normal operation). | 26 | Possible damage to transformer protection devices. | To be updated | Examine drain cocks for signs of recent leaks. |  | Examine drain cocks for signs of recent leaks. | Examine in conjunction with other tasks | TX oil leak repair. | ZS Inspect |  | 0 | N/A | 2 | 0.01 | 2.01 | 5000 | 3650 | 907960 | Original MRA Ccf:2; Ccf:0.01; Pop:5000; MTBF:907960.2; Cfint:3650; OptimumInt: 13978.52 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 15 | 80 | 0 | 0 | 200 | 200 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to leaking fins/radiator. (Normal operation). | 27 | Possible damage to transformer protection devices. | To be updated | Examine radiators/fins, main tank and bushing gaskets for signs of recent leaks. |  | Examine radiators/fins for signs of recent leaks. | Part of exisiting inspection regime | TX oil leak repair. # TX replace. | 6yr Maint. |  | 0 | N/A | 8 | 0 | 0 | 4000 | 7 | 182500 | Assume 8 fins per Tx. Original MRA Ccf:8; Ccf:0; Pop:4000; MTBF:182500; Cfint:7; OptimumInt: 1341.83 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 05) Provide protective earth connection to transformer. | a) Does not provide protective earth connection to transformer. | TANK not effectively earthed due to corroded or broken connection. (Normal operation). | 28 | Possible failure of protection devices. Electric shock. | To be updated | Examine visually earth connections to transformer for security. |  | Examine visually neutral/earth bonds and connections on transformer are undamaged and secure. |  | Earth connection repair / replace. | 6yr Maint. |  | 0 | N/A | 0.1 | 0 | 0.1 | 500 | 3650 | 1825000 | Original MRA Ccf:0.1; Ccf:0; Pop:500; MTBF:1825000; Cfint:3650; OptimumInt: 2148 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 10 | 90 | 40 | 0 | 1500 | 11500 | 10000 | 0 | 1 | 0 | 0 | 0 | 0 | Earthing
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN not operating due to motor circuit breaker defective. (Normal operation). | 34 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. | Replace upon failure. | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 0.37 | 1.45 | 0 | 590 | 0 | 118324 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 01) Transformation of power from primary to secondary voltage within assigned rating. | b) Does not withstand through fault current. | CORE loss of clamping pressure due to core shrinkage. (Normal operation). | 36 | Winding failure, loss of supply | To be updated | N.S.M. |  | N.S.M. | except as noted in failure mode 140 | TX replace. # TX repair. | N.S.M. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 06) Operates within maximum noise level. | a) Noise level above maximum acceptable level. | AUXILLARY COOLING SYSTEM excess / unusual noise due to fan bearing. (Normal operation). | 37 | Noise complaints, eventual equipment failure if not actioned. | To be updated | N.S.M. |  | N.S.M. |  | TX cooling fan repair / replace. | N.S.M. |  | 0 | N/A | 0 | 0.91 | 0.91 | 590 | 0 | 236648 | Original MRA Ccf:70; Ccf:1; Pop:350; MTBF:1799.296; Cfint:365; OptimumInt: 175.8365 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 5 | 90 | 40 | 0 | 1000 | 3000 | 2000 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor | Noise
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to external CT terminals leak. (Normal operation). | 42 | Possible damage to transformer. | To be updated | Examine transformer external CT terminals for signs of oil leaks |  | Examine transformer external CT terminals for signs of oil leaks |  | TX oil leak repair. | 6yr Maint. |  | 0 | N/A | 10 | 0.01 | 10.01 | 500 | 3650 | 18232 | Original MRA Ccf:10; Ccf:0.01; Pop:500; MTBF:18231.77; Cfint:3650; OptimumInt: 2923.849 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 15 | 95 | 100 | 0 | 1500 | 1500 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OIL GAUGE incorrect indication due to dirty sight glass (Normal operation). | 43 | Loss level indication. | To be updated | N.S.M. |  | N.S.M. |  | TX sight glass clean / repair / replace. | N.S.M. |  | 0 | N/A | 8.73 | 0 | 8.73 | 590 | 0 | 24668 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 09) To provide controlled relief of internal pressure. | a) Does not provide controlled relief of internal pressure. | PRESSURE RELIEF VALVE fails to operate due to jammed (Normal operation). | 44 | Possible rupture of tank, loss of oil. | To be updated | Visually examine the valve for wildlife nesting. |  | Visually examine the transformer main tank valve for wildlife nesting. |  | TX Qualitrol repair / replace. | 1yr DGA Oil Sample |  | 0 | N/A | 0 | 0.18 | 0.18 | 0 | 0 | 0 | New design.. Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 2923.849 | N | Y | Y | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | OIL contaminated due to damaged explosion vent. (Normal operation). | 45 | Possible damage to transformer. | To be updated | Examine explosion vent and diaphram for signs of damage. |  | Check explosion vent for correct diaphragm, and examine for cracks and signs of damage. | Carried out as part of out of service maintenance. <10% task effectiveness from the ground. | TX explosion vent repair / replace. | 6yr Maint. |  | 12000 | Min Impact / Min Equipment Damage | 0.6 | 0 | 0 | 330 | 7200 | 200750 |  | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 75 | 110 | 128.33 | 500 | 612500 | 600000 | 1825.2352 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to pressure relief device leaks. (Normal operation). | 46 | Possible damage to transformer. | To be updated | Examine pressure relief device for recent leaks. |  | Examine pressure relief device for recent leaks. | TRD suggested love tap with hammer if not bad. | TX oil leak repair. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | No failures seen as yet.. Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 09) To provide controlled relief of internal pressure. | a) Does not provide controlled relief of internal pressure. | EXPLOSION VENT unsuitable due to incorrect material fitted. (Normal operation). | 47 | Possible rupture of tank, loss of oil. | To be updated | Check explosion vent for correct diaphragm. |  | Check explosion vent for correct diaphragm, and examine for cracks and signs of damage. | Should be corrected prior to commisioning. | TX explosion vent repair / replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 |  | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 06) Operates within maximum noise level. | a) Noise level above maximum acceptable level. | AUXILLARY COOLING SYSTEM excess / unusual noise due to pump bearing. (Normal operation). | 52 | Noise complaints, eventual equipment failure if not actioned. | To be updated | Examine transformer cooling pumps (where fitted) for excessive noise. |  | Examine transformer cooling pumps (were fitted) for excessive noise. |  | TX cooling pump repair / replace. | ZS Inspect |  | 0 | N/A | 0 | 0.18 | 0.18 | 590 | 1000 | 1196389 | Original MRA Ccf:0.1; Ccf:0; Pop:200; MTBF:730000; Cfint:1000; OptimumInt: 6745.594 | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 90 | 40 | 0 | 10000 | 21000 | 11000 | 0 | 1 | 0 | 0 | 0 | 0 | Peripheral |  | Noise
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 06) Operates within maximum noise level. | a) Noise level above maximum acceptable level. | TX ANCILLIARY COMPONENTS excess noise due to loose components. (Normal operation). | 53 | Noise complaints, possible equipment failure if not actioned. | To be updated | Examine transformer accessories for excess noise/vibration. |  | Examine transformer accessories for excess noise/vibration. |  | TX vibration (noise) repair. | ZS Inspect |  | 0 | N/A | 1.27 | 0 | 1.27 | 590 | 365 | 169567 | No CF constant. We used an estimate of 12 months. Original MRA Ccf:120; Ccf:0.5; Pop:500; MTBF:1514.523; Cfint:365; OptimumInt: 0 | N | Y | Y | N | N | Y |  |  |  |  | Substation Crew (2) | 5 | 90 | 40 | 0 | 50 | 800 | 750 | 0 | 1 | 0 | 0 | 0 | 0 | Peripheral |  | Noise
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 06) Operates within maximum noise level. | a) Noise level above maximum acceptable level. | CORE excess noise due to lamination loose. (Normal operation). | 54 | Noise complaints, possible equipment failure if not actioned. | To be updated | Examine transformer for excess noise/vibration. |  | Examine transformer for excess noise/vibration. |  | TX repair. | ZS Inspect |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | See loss of clamping pressure.. Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 6745.594 | N | Y | Y | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 06) Operates within maximum noise level. | a) Noise level above maximum acceptable level. | CORE excess noise due to loss of core clamping. (Normal operation). | 55 | Noise complaints, possible equipment failure if not actioned. | To be updated | Examine transformer for excess noise/vibration. |  | Examine transformer for excess noise/vibration. |  | TX replace. # TX repair. | ZS Inspect |  | 0 | N/A | 0.12 | 1 | 1.12 | 500 | 2190 | 162946 | Original MRA Ccf:0.12; Ccf:1; Pop:500; MTBF:162946.4; Cfint:2190; OptimumInt: 901 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 90 | 40 | 0 | 200000 | 400000 | 200000 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | TX BREATHER moisture ingress due to undersized. (Normal operation). | 57 | Possible ingress of moisture transformer transformer. | To be updated | N.S.M. |  | N.S.M. |  | TX breather upgrade. | N.S.M. |  | 0 | N/A | 1.64 | 1.09 | 2.73 | 590 | 0 | 78883 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | N | N | N | N | N | N | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank |  | breather failure
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 05) Provide protective earth connection to transformer. | a) Does not provide protective earth connection to transformer. | TANK not effectively earthed due to damaged earth bonds. (Normal operation). | 58 | Tank hots spots, loss of equipotential (touch potential) | To be updated | Examine earth bonds on transformer are undamaged and secure. |  | Examine visually neutral/earth bonds and connections on transformer are undamaged and secure. |  | Earth connection repair / replace. | 6yr Maint. |  | 0 | N/A | 2.18 | 0 | 2.18 | 590 | 0 | 98784 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0. Eight of 12 failures seen relate to warranty defects | N | Y | Y | N | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Earthing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 05) Provide protective earth connection to transformer. | a) Does not provide protective earth connection to transformer. | TANK not effectively earthed due to vandalism. (Normal operation). | 59 | Tank hots spots, loss of equipotential (touch potential). | To be updated | Examine bonds on transformer are undamaged and secure. |  | Examine visually neutral/earth bonds and connections on transformer are undamaged and secure. |  | Earth connection repair / replace. | 6yr Maint. |  | 0 | N/A | 0 | 5 | 5 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:5; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Earthing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 05) Provide protective earth connection to transformer. | a) Does not provide protective earth connection to transformer. | CORE not effectively earthed due to burnt off. (Normal operation). | 60 | Excessive transformer losses and gassing of oil. | To be updated | Test transformer oil sample for dissolved gases. (C2H4/C2H6 Ratio > 3) (C2H2/C2H4 Ratio >3) | Oil Sample | Test the transformer oil sample from main tank valve for dissolved gases. | Relevant to commissioning / after major repair. Ensure core earth is repaired and connected prior to re-energisation after working on core/in tank. | TX repair. | 1yr DGA Oil Sample |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Earthing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 05) Provide protective earth connection to transformer. | a) Does not provide protective earth connection to transformer. | CORE not effectively earthed due to missing / open bond. (Normal operation). | 61 | Excessive transformer losses and gassing of oil. | To be updated | Test transformer oil sample for dissolved gases. (C2H4/C2H6 Ratio > 3) (C2H2/C2H4 Ratio >3) | Oil Sample | Test the transformer oil sample from main tank valve for dissolved gases. |  | TX repair. | 1yr DGA Oil Sample |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Earthing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN not operating due to seized fan. (Normal operation). | 62 | Overheating alarm, reduction in transformer life. | To be updated | Examine fans for correct operation. |  | Examine fans for correct operation and excessive noise. | Replace defective fans and ensure thermal breaker setting is correct. | TX cooling fan repair / replace. | ZS Inspect |  | 0 | N/A | 1.09 | 6.55 | 0 | 590 | 500 | 28187 | Original MRA Ccf:75; Ccf:5; Pop:3000; MTBF:13687.5; Cfint:500; OptimumInt: 566. Data now on a per TX basis. Task period > CF interval ! | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 10 | 98 | 40 | 76.67 | 1000 | 2000 | 1000 | -19625.8965 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN not operating due to water in terminal box (Normal operation). | 63 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. | Failure data indicates task no longer valid as optimum > 143,000 days | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 0.36 | 0.18 | 0 | 590 | 1040 | 398796 | Original MRA Ccf:35; Ccf:9; Pop:1500; MTBF:12443.18; Cfint:1040; OptimumInt: 562 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 10 | 85 | 40 | 76.67 | 300 | 1400 | 1100 | -745.8547 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN not operating due to wiring defect. (Normal operation). | 64 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. | Vibration, damage. | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 3.45 | 3.64 | 0 | 590 | 0 | 30374 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | N | N | Y | N | N | N | N |  | N | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN not operating due to corroded case. (Normal operation). | 66 | Makes reconditioning / repair difficult | To be updated | N.S.M. |  | N.S.M. | Assessed off system regarding for viability of repair. | TX cooling fan repair / replace. | N.S.M. |  | 0 | N/A | 1.45 | 0.18 | 0 | 590 | 0 | 132117 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0. Data on a per Tx basis. Examination / check task not valid as task period > CF interval. | Y | N | N | Y | N | N | N | N |  | N | Substation Crew (2) | 10 | 98 | 40 | 0 | 1000 | 2000 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to motor circuit breaker incorrectly set. (Normal operation). | 68 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. |  | TX cooling control repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0 | 0 | 0 | 200 | 0 | 0 | No CF interval use a failure finding task.. Original MRA Ccf:0; Ccf:0; Pop:200; MTBF:6083.333; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 |  |  | 0 | 600 | 54600 | 4000 | 0 | 1 | 250 | 506944 | 600 | 0.18 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to corroded case. (Normal operation). | 69 | Makes reconditioning / repair difficult | To be updated | N.S.M. |  | N.S.M. | Assessed of system regarding viability of repair. | TX cooling pump repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0 | 0 | 0 | 590 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | N | N | Y | N | N | N | N |  | N | Substation Crew (2) | 0 |  |  | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to seized pump. (Normal operation). | 71 | Overheating alarm | reduction in transformer life. | N.S.M. |  | N.S.M. |  | TX cooling pump repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0.18 | 0.18 | 0.36 | 590 | 0 | 598194 | No failures have been seen as yet on pumps. Original MRA Ccf:0.1; Ccf:0; Pop:200; MTBF:730000; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 |  |  | 0 | 1000 | 52000 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to water in terminal box (Normal operation). | 72 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. |  | TX cooling control repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0.18 | 0.18 | 0.36 | 590 | 0 | 598194 | Original MRA Ccf:0; Ccf:4; Pop:200; MTBF:18250; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 |  |  | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to wiring defect. (Normal operation). | 73 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. | Vibration, damage. new installs have monitoring and alarming. | TX cooling control repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0.55 | 0.18 | 0.73 | 590 | 0 | 295000 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 |  |  | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to motor circuit breaker defective. (Normal operation). | 74 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. |  | TX cooling pump repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0.18 | 1.09 | 1.27 | 590 | 0 | 169567 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 |  |  | 0 | 600 | 54600 | 4000 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to sheared impeller shaft (Normal operation). | 75 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. |  | TX cooling pump repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to motor soft starter malfunction. (Normal operation). | 76 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. | alarm on newer installations. | TX cooling pump repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0.36 | 2.55 | 2.91 | 590 | 0 | 74003 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | RADIATOR ineffective cooling due to valve inoperable. (Normal operation). | 77 | Overheating alarm, reduction in transformer life. | To be updated | N.S.M. |  | N.S.M. |  | TX radiator repair. | N.S.M. |  | 50000 | Network disruption (30 min) | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING damaged porcelain due to wildlife. (Normal operation). | 80 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | N.S.M. |  | N.S.M. | Installation of additional insulated vermin barriers on insulators after flashover. | TX bushing clean / repair. # TX bushing replace. # TX bushing vermin guard install. | N.S.M. |  | 0 | N/A | 1.27 | 0.55 | 1.82 | 590 | 0 | 118324 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | Y | N | Y | N | N | N | N |  | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING internal fault due to moisture ingress from defective seals. (Normal operation). | 82 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | Test and record DDF (Dielectric Dissipation Factor) of oil filled bushing. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. | DDF | Test and record DDF (Dielectric Dissipation Factor) of oil filled bushing. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. | see bushing delamintation (age deterioration) | TX bushing clean / repair. # TX bushing replace. | 6yr Maint. |  | 0 | N/A |  |  |  |  | 3650 | 0 | see code 100 | N | Y | Y | Y | N | Y | [5 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING internal fault due to contaminated oil. (Normal operation). | 83 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | Test and record condensor type transformer bushing insulation resistance at 2.5kV | IR | Test and record condensor type transformer bushing Insulation Resistance at 2.5kV | Needs to be at 2.5kV rather than 5kV to enable direct comparision with historical results | TX bushing clean / repair. # TX bushing replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | See code 100 | N | Y | N | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING internal fault due to loss of capacitive grading. (Normal operation). | 84 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | Test and record DDF (Dielectric Dissipation Factor) of oil filled bushing. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. | DDF | Test and record DDF (Dielectric Dissipation Factor) of oil filled bushing. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. |  | TX bushing clean / repair. # TX bushing replace. | 6yr Maint. |  | 0 | N/A |  |  |  |  | 0 | 0 | see code 143 for op data. | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 30 | 98 | 1000 | 0 | 20000 | 520000 | 500000 | 0 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to tank bushing leaks. (Normal operation). | 86 | Possible damage to transformer. | To be updated | N.S.M. |  | N.S.M. | Oil leaks become visible in other areas (tapchanger etc) | TX bushing replace. | N.S.M. |  | 0 | N/A | 10.18 | 0 | 0 | 590 | 0 | 21154 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | WINDING insulation failure due to overloading (Heating). (Normal operation). | 89 | Accelerated aging of paper insulation. | Loss of paper strength in conjunction with vibration or through fault leads to possible shorted turns, damage to transformer. Diff protection and/or Buchholz relay operates. | Check and record winding temperature. |  | Check and record oil and winding temperature. | minor overloading detectable in DGA but significant overloading will have impact very quickly. | TX oil sample required. | ZS Inspect |  | 0 | N/A |  | 0.1 | 0 | 590 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | N | N | Y | Y | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN not operating due to OTI switch maloperation. (Normal operation). | 91 | Overheating alarm, reduction in transformer life. | To be updated | Test OTI/WTI switch triggers fan and pump operation with associated alarms/trip outputs. |  | Test OTI switch triggers fan and pump operation with associated alarms/trip outputs. |  | TX thermal indicator repair / replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 350 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:350; MTBF:12775; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | Y |  | Substation Crew (2) | 120 | 98 | 100 | 0 | 3000 | 23000 | 10000 | 0 | 1 | 350 | 77896 | 3000 | 1.64 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to thermal indicator switch maloperation. (Normal operation). | 92 | Overheating alarm, reduction in transformer life. | To be updated | Test OTI switch triggers fan and pump operation with associated alarms/trip outputs. |  | Test OTI switch triggers fan and pump operation with associated alarms/trip outputs. |  | TX thermal indicator repair / replace. | 6yr Maint. |  | 50000 | Network disruption (30 min) | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | Y |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OIL GAUGE incorrect indication due to jammed pointers (corrosion of aluminium) (Normal operation). | 95 | Loss level indication. | To be updated | N.S.M. |  | N.S.M. | It was assumed that when checking for oil leaks the oil level would be checked for correct operation. | TX conservator repair. | N.S.M. |  | 0 | N/A | 1.45 | 0.18 | 1.63 | 590 | 0 | 132117 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OIL GAUGE incorrect indication due to damaged floats (Normal operation). | 96 | Loss level indication. | To be updated | N.S.M. |  | N.S.M. |  | TX conservator repair. | N.S.M. |  | 0 | N/A | 0.18 | 0 | 0.18 | 590 | 0 | 1196389 | No CF fix when failed.. Original MRA Ccf:0; Ccf:1; Pop:200; MTBF:73000; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OIL GAUGE incorrect indication due to blocked sight glass. (Normal operation). | 97 | Loss level indication. | To be updated | N.S.M. |  | N.S.M. |  | TX sight glass clean / repair / replace. | N.S.M. |  | 0 | N/A | 0.55 | 0 | 0.55 | 590 | 0 | 391545 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 01) Transformation of power from primary to secondary voltage within assigned rating. | a) Does not transform power from primary to secondary voltage. | WINDING no output power due to continuity failure. (Normal operation). | 11 | Loss of supply to system. | To be updated | N.S.M. |  | N.S.M. | On site | TX replace. | N.S.M. |  | 600000 | Min Impact / Major Equipment Damage | 0.36 | 0.3 | 0.66 | 770 | 0 | 425833 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 600000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | INTERNAL BUSHING damaged porcelain due to movement (Normal operation). | 99 | Flashover, possible secondary damage. Loss of supply from transformer. | To be updated | N.S.M. |  | N.S.M. |  | TX bushing replace. | N.S.M. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING internal fault due to delamination (age deterioration) (Normal operation). | 100 | Flashover, possible secondary damage and flying porcelain. Loss of supply from transformer. | To be updated | Test and record DDF (Dielectric Dissipation Factor) of oil filled bushing. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. | DDF | Test and record DDF (Dielectric Dissipation Factor) of oil filled bushing. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. | Diagnostic to cover other internal failure modes. Levels above 10 milliradians are of concern. 15 is the conditional failure limit. | TX bushing clean / repair. # TX bushing replace. | 6yr Maint. |  | 120000 | Min Impact / Med Equipment Damage | 4 | 0.6 | 0 | 770 | 2920 | 61098 |  | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 90 | 95 | 110 | 440 | 25000 | 175000 | 30000 | 2249.9336 | 1 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to vandalism. (Normal operation). | 101 | Possible damage to transformer. | To be updated | N.S.M. |  | N.S.M. |  | TX oil leak repair. | N.S.M. |  | 0 | N/A | 0.2 | 0 | 0.2 | 0 | 0 | 0 | Original MRA Ccf:0.2; Ccf:; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | N | N | N | N | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | AUXILIARY COOLING SYSTEM not operating due to oil pump starter fail. (Normal operation). | 108 | oil pumps will not start | Loss of forced oil cooling | N.S.M. |  | N.S.M. | will become evident when pump/fans undergo an operational test | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 0 | 0.18 | 0 | 590 | 0 | 1196389 |  | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 1 | 99 | 40 | 0 | 1000 | 3000 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | CABLE END BOX failure of tank to contain oil due to deteriorated gaskets. (Normal operation). | 109 | oil leaks. | Possible ingress of moisture. Loss of oil level in oil level in oil filled cable endboxes which may lead to a flashover and loss of supply. | Examine transformer oil filled cable endbox for signs of external oil leaks |  | Examine all of transformer for signs of external oil leaks and check conservator oil level. |  | TX end box repair / replace. | ZS Inspect |  | 600000 | Min Impact / Major Equipment Damage | 1.27 | 0 | 1.27 | 590 | 2190 | 169567 |  | Y | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 70 | 40 | 0 | 20000 | 622000 | 2000 | 484 | 0 | 0 | 0 | 0 | 0 | Bushing | Major | Cable
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING damaged porcelain due to mechanical impact (Normal operation). | 110 | damaged porcelain. | Possible ingress of moisture through crack path leading to bushing failure with possible secondary damage and flying porcelain. Loss of supply from transformer. | Examine all transformer bushing surfaces for damage. |  | Examine all transformer bushing surfaces for damage. | Package into routine substation inspections | TX bushing clean / repair. # TX bushing replace. | ZS Inspect |  | 120000 | Min Impact / Med Equipment Damage | 1.5 | 0 | 1.5 | 770 | 1095 | 187367 |  | Y | Y | N | Y | N | Y |  |  |  |  | Substation Crew | 5 | 75 | 110 | 0 | 3000 | 153000 | 30000 | 697 | 0 | 0 | 0 | 0 | 0 | Bushing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL FLOW INDICATOR not operating due to mechanical failure. (Normal operation). | 113 | loss of flow indication. |  | N.S.M. |  | N.S.M. |  | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 1.64 | 0.18 | 1.82 | 590 | 0 | 118324 |  | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL FLOW INDICATOR leaks due to corroded / damaged. (Normal operation). | 114 |  |  | Examine transformer for signs of external oil leaks. |  | Examine all of transformer for signs of external oil leaks and check conservator oil level. | Task period is -20,450 days - may not be valid. | TX cooling control repair / replace. | ZS Inspect |  | 12000 | Min Impact / Min Equipment Damage | 0.18 | 0 | 0.18 | 590 | 760 | 1196389 |  | N | N | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 75 | 40 | 0 | 2000 | 14000 | 0 | -792 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL FLOW RELAY not operating due to internal defect. (Normal operation). | 115 |  |  | N.S.M. |  | N.S.M. | Task optimum of -4559 days indicates no valid PM task. | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 0.18 | 0 | 0.18 | 590 | 3650 | 1196389 |  | Y | N | N | Y | N | N | N | N |  | N | Substation Crew (2) | 10 | 75 | 100 | 0 | 2000 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OIL GAUGE incorrect indication due to ingress of moisture (Normal operation). | 116 |  |  | N.S.M. |  | N.S.M. |  | TX conservator repair. | N.S.M. |  | 0 | N/A | 0 | 0.18 | 0.18 | 590 | 0 | 1196389 |  | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OIL GAUGE incorrect indication due to vibration mounts fail (Normal operation). | 117 | difficult to read oil guage | guage may be damaged / leak. | N.S.M. |  | N.S.M. |  | TX conservator repair. | N.S.M. |  | 0 | N/A | 0.18 | 0 | 0.18 | 590 | 0 | 1196389 |  | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | OIL PUMP not operating due to internal defect. (Normal operation). | 118 | Overheating alarm, | reduction in transformer life. | N.S.M. |  | N.S.M. |  | TX cooling pump repair / replace. | N.S.M. |  | 50000 | Network disruption (30 min) | 0.18 | 0.55 | 0.73 | 590 | 0 | 295000 |  | Y | N | N | Y | N | N | N | N |  | N | Substation Crew (2) | 0 |  |  | 0 | 10000 | 60000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | PIPEWORK leaks due to corrosion. (Normal operation). | 119 |  |  | N.S.M. |  | N.S.M. |  | TX oil leak repair. | N.S.M. |  | 12000 | Min Impact / Min Equipment Damage | 0.1 | 0 | 0.1 | 770 | 3650 | 2810500 | Unsure ever seen any in EE | Y | N | N | Y | N | N | N | N |  | N | Substation Crew | 5 | 85 | 110 | 0 | 500 | 17500 | 5000 | -5270 | 0 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 09) To provide controlled relief of internal pressure. | a) Does not provide controlled relief of internal pressure. | PRESSURE RELIEF VALVE fails to operate due to corroded / damaged. (Normal operation). | 120 |  |  | N.S.M. |  | N.S.M. | was Visually examine the valve for leaks / damage. but task period -ve. Commissioning operational check? | TX Qualitrol repair / replace. | N.S.M. |  | 0 | N/A | 0.18 | 0 | 0.18 | 590 | 2190 | 1196389 |  | Y | N | N | Y | N | N | N | N |  | N | Substation Crew (2) | 5 | 75 | 40 | 0 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | TANK failure to contain oil due to broken capillary tube. (Normal operation). | 121 |  |  | N.S.M. |  | N.S.M. |  | TX oil leak repair. | N.S.M. |  | 0 | N/A | 0.18 | 0 | 0.18 | 770 | 0 | 1561389 | warranty repair | Y | N | N | N | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | TX LINK BOX loss of insulation due to degradation of insulation. (Normal operation). | 132 | Tx trips |  | N.S.M. |  | N.S.M. | Possible design issue, cable termination arrangement or foreign body?? | TX end box repair / replace. | N.S.M. |  | 0 | N/A | 0 | 0.18 | 0.18 | 8 | 0 | 16222 | 1 Incident at Camperdown Zn | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | TBC
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | COOLING FAN excess / unusal noise due to defective bearing. (Normal operation). | 134 | noisy fan | Overheating alarm, reduction in transformer life. | Examine fans for excessive noise. |  | Examine fans for correct operation and excessive noise. |  | TX cooling fan repair / replace. | ZS Inspect |  | 0 | N/A | 1.09 | 0 | 0 | 590 | 500 | 197569 |  | N | N | N | Y | Y | [5 empty] | Substation Crew (2) | 10 | 50 | 40 | 76.67 | 1000 | 2000 | 1000 | -91.7478 | 0 | 0 | 0 | 0 | 0 |  |  | noise
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | CABLE END BOX flashover due to excessive moisture ingress in end box. (Normal operation). | 142 | Reduction in insulation co-ordination | Loss of supply | Examine air end box for signs of degredation and moisture ingress. |  | Examine air end box for signs of degredation and moisture ingress. | Intention to be completed as part of diag maintenance. | TX end box repair / replace. | 6yr Maint. |  | 120000 | Min Impact / Med Equipment Damage | 0.1 | 0 | 0.1 | 10 | 3650 | 36500 |  | Y | Y | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 90 | 95 | 110 | 0 | 100 | 150100 | 30000 | 1889 | 0 | 0 | 0 | 0 | 0 | Bushing | Major | cable
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | EXTERNAL BUSHING internal fault due to DLA test point earthing defective (Normal operation). | 143 | Delay/problems with testing | Flashover/burning/arcing at DLA Point. Possible bushing failure and loss of supply. | Examine DLA test point for signs of damage. |  | Examine DLA test point for signs of damage. | intention to be completed as part of diag maintenance. | TX bushing clean / repair. # TX bushing replace. | 6yr Maint. |  | 600000 | Min Impact / Major Equipment Damage | 0.5 | 0 | 0 | 770 | 3650 | 562100 |  | N | Y | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 15 | 95 | 110 | 165 | 3000 | 633000 | 30000 | 2538.3047 | 0 | 0 | 0 | 0 | 0 | Bushing | Minor | testing
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | b) Does not provide primary containment of insulating medium. | PIPEWORK leaks due to defective valve. (Normal operation). | 145 | Oil leak | Loss of transformer function | Examine transformer pipework including valves and flanges for signs of external oil leaks. |  | Examine transformer pipework including valves and flanges for signs of external oil leaks. |  | TX oil leak repair. | 6yr Maint. |  | 12000 | Min Impact / Min Equipment Damage | 60 | 0 | 60 | 770 | 3650 | 4684 | Based on typical leaks seen time to drain to low oil trip 10years | Y | N | N | Y | N | Y |  |  |  |  | Substation Crew | 5 | 90 | 110 | 0 | 500 | 22500 | 10000 | 1593 | 0 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | OIL accelerated degredation due to excessive oil temperature. (Normal operation). | 146 | Hot Oil | accelerated degradation of winding and oil. | Check and record oil temperature. |  | Check and record oil and winding temperature. |  | TX repair. | ZS Inspect |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | Y | Y | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 05) Provide protective earth connection to transformer. | a) Does not provide protective earth connection to transformer. | CORE multiple earth points due to core/frame insulation defect. (Normal operation). | 147 | Circulating currents and excessive heating. | Damage to insulation | Test transformer oil sample for dissolved gases. (CH4/H2 Ratio 1-3) (C2H4/C2H6 Ratio >3) | Oil Sample | Test the transformer oil sample from main tank valve for dissolved gases. |  | TX replace. # TX repair. | 1yr DGA Oil Sample |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Earthing |  | circulating current
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 06) Operates within maximum noise level. | a) Noise level above maximum acceptable level. | AUXILLARY COOLING SYSTEM excess / unusual noise due to loose fan mounting. (Normal operation). | 148 | Metal on metal vibration creating noise | Angry residents | Examine fans for excessive noise. |  | Examine fans for correct operation and excessive noise. |  | TX cooling fan repair / replace. | ZS Inspect |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | Y | N | N | N | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | noise
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | BLADDER (INTERNAL) obstructing breather due to rupture. (Normal operation). | 149 | Bladder fills with oil and covers beather pipe | Increased oil leaks and potential protection operation due to over pressure | N.S.M. |  | N.S.M. | Run to failure. Some TX fitted with bladder fail alarm. Lindsay Mc to determine if possible to test bladder. | TX bladder replace. | N.S.M. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tank | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | BLADDER (INTERNAL) obstructing breather due to incorrect oil filling procedure (Normal operation). | 150 | Bladder fills with oil and covers beather pipe | Increased oil leaks and potential protection operation due to over pressure | N.S.M. |  | N.S.M. | Run to failure. Some TX fitted with bladder fail alarm. Lindsay Mc to determine if possible to test bladder. | TX oil leak repair. | N.S.M. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tank | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | TX BREATHER moisture ingress due to EZY dry bottle cracked. (Normal operation). | 151 | Silca gel degrades faster | Entry of moisture into conservator and accelerated aging of oil on free breathing TX. | Examine silica gel in EZY dry breather bottle for at least 50% blue colour. |  | Examine silica gel for at least 50% blue colour. |  | TX silica gel replace. | ZS Inspect |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | Y | N | N | Y | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tank | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | BLADDER (EXTERNAL) ruptured due to pressure relief device fail. (Normal operation). | 152 | Loss of nitrogen from bladder | Dehydrating breather limits moisture ingress. | N.S.M. |  | N.S.M. | Lindsay McPherson to confirm conservator overpressure relief system is duplicated. | TX Qualitrol repair / replace. | N.S.M. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | N | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | TBC
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 07) Provide pressure equalisation due to oil expansion / contraction via dehydrating breather. | a) Does not provide dehydrated air via breather. | BLADDER (EXTERNAL) ruptured due to age degradation. (Normal operation). | 153 | Loss of nitrogen from bladder | Dehydrating breather limits moisture ingress. | Check bladder integrity by visual inspection and checking nitrogen circuit silica gel. |  | Check bladder integrity by visual inspection and checking nitogen circuit silica gel. | Operating transformer will have higher temperature and bag will be naturally inflated. | TX bladder replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | N | N | N | N | N | Y |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 09) To provide controlled relief of internal pressure. | b) Unintended rupture | EXPLOSION VENT ruptured or cracked due to fatigue (Normal operation). | 155 | Ingress of air and moisture | accelerated degradation of winding and oil. | Examine explosion vent for cracks. |  | Check explosion vent for correct diaphragm, and examine for cracks and signs of damage. |  | TX explosion vent repair / replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | N | N | Y | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tank
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OTI inoperative due to broken capillary tube. (Normal operation). | 156 | Loss of overtemperature alarm, cooling does not operate. | To be updated | N.S.M. |  | N.S.M. |  | TX thermal indicator repair / replace. | N.S.M. |  | 0 | N/A | 1.27 | 2.55 | 3.82 | 590 | 0 | 56374 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 8 of the 21 latest defects are warranty related. Majority of non warranty are on older Tx styles. | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OTI false alarms due to vibration mounts fail (Normal operation). | 157 | False transformer overtemperature trip | Possible loss of supplky if substation is already configured at N | Examine OTI vibration mounts for signs of degradation. |  | Examine thermal indicator vibration mounts for signs of degradation. |  | TX thermal indicator repair / replace. | ZS Inspect |  | 0 | N/A | 0.91 | 0.36 | 1.27 | 590 | 3650 | 169567 | Original MRA Ccf:45; Ccf:0.1; Pop:250; MTBF:2023.282; Cfint:3650; OptimumInt: 1418 | Y | N | N | Y | N | Y |  |  |  |  | Substation Crew (2) | 5 | 95 | 20 | 0 | 200 | 1200 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | TBC | Spurious trip
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OTI false alarms due to ingress of moisture. (Normal operation). | 158 | False transformer overtemperature trip |  | N.S.M. |  | N.S.M. | Warranty Check ? | TX thermal indicator repair / replace. | N.S.M. |  | 0 | N/A | 0.18 | 0.18 | 0.36 | 590 | 0 | 598194 | Leak is rapid upon gasket failure and leaks to false alarm indication. Both events have been seen as warranty defects and none recorded on older Tx. | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | TBC | Spurious trip
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OTI false alarms due to internal defect. (Normal operation). | 159 |  |  | N.S.M. |  | N.S.M. | Any indicators? | TX thermal indicator repair / replace. | N.S.M. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | All warranty defects - 1 emergency, 3 urgent, 3 prioritise, 6 next mtce, 1 followup | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | TBC | Spurious trip
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OTI incorrect indication due to age degradation. (Normal operation). | 160 | False temperature reading - obvious where significantly different to WTI. |  | N.S.M. |  | N.S.M. | Replace when found. | TX thermal indicator repair / replace. | N.S.M. |  | 0 | N/A | 0.73 | 0.18 | 0.91 | 590 | 0 | 236648 |  | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | OTI inoperative due to internal defect. (Normal operation). | 161 | no temperature reading evident. |  | N.S.M. |  | N.S.M. | Warranty Check task | TX thermal indicator repair / replace. | N.S.M. |  | 0 | N/A | 1.45 | 0.73 | 2.18 | 590 | 0 | 98784 | All 12 events are warranty related | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | WTI CURRENT TRANSFORMER incorrect output due to internal defect. (Normal operation). | 164 | Loss of overtemperature alarm, cooling does not operate. |  | N.S.M. |  | N.S.M. |  | TX thermal indicator repair / replace. | N.S.M. |  | 0 | N/A | 0 | 0.18 | 0.18 | 590 | 0 | 1196389 |  | Y | N | N | Y | N | N | N | N |  | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | Minor
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 04) Provides measurement of transformer operating parameters. | a) Does not provide measurement of transformer operating parameters. | TX CONTROL indication failure due to blown fuse / bulb. (Normal operation). | 165 |  |  | Check lights for correct operation. |  | Check lights for correct operation. | Warranty Schedule | TX control cabinet repair. | ZS Inspect |  | 0 | N/A | 0 | 0.73 | 0.73 | 590 | 0 | 295000 |  | Y | N | N | N | Y | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Peripheral
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 10) Provides environmental protection of control cabinet to rating IP53 | a) Does not provide environmental protection of control cabinet to rating IP53 | CONTROL CABINET contaminant ingress due to heater failed. (Normal operation). | 166 |  |  | Check control cabinet heater for correct operation. |  | Check control cabinet heater for correct operation. | Warranty Schedule | TX control cabinet repair. | ZS Inspect |  | 0 | N/A | 0 | 0.55 | 0.55 | 590 | 0 | 391545 | All warranty Defects | N | N | N | Y | N | N | N | N | Y |  | Substation Crew (2) | 2 | 75 | 60 | 0 | 200 | 10200 | 0 | 0 | 1 | 590 | 391545 | 200 | 0.55 | Peripheral
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 10) Provides environmental protection of control cabinet to rating IP53 | a) Does not provide environmental protection of control cabinet to rating IP53 | CONTROL CABINET contaminant ingress due to door seal failure. (Normal operation). | 167 |  |  | N.S.M. |  | N.S.M. |  | TX control cabinet repair. | N.S.M. |  | 0 | N/A | 0.73 | 0 | 0.73 | 590 | 0 | 295000 |  | N | N | N | Y | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Peripheral
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 10) Provides environmental protection of control cabinet to rating IP53 | a) Does not provide environmental protection of control cabinet to rating IP53 | CONTROL CABINET contaminant ingress due to corrosion. (Normal operation). | 168 | damaged components | Failures earlier in life than expected of ancillary components leading to increased corective. | N.S.M. |  | N.S.M. | Warranty Inspection? | TX control cabinet repair. | N.S.M. |  | 0 | N/A | 0.55 | 0 | 0.55 | 590 | 0 | 391545 |  | N | N | N | N | N | N | N | N | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Peripheral
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 03) Provides cooling of transformer. | a) Does not provide cooling of transformer. | AUXILIARY COOLING SYSTEM not operating due to defective contactor. (Normal operation). | 170 | Loss of cooling or noise complaints from intermittent operation | Eventual control / contactor equipment failure if not actioned. Loss of operation of fans and/or oil pumps. | N.S.M. |  | N.S.M. | Optimum for proposed task "Examine transformer fans and cooling pumps (were fitted) for excessive noise." was -452 days -> no a valid task due to low failure rate => NSM | TX cooling control repair / replace. | N.S.M. |  | 0 | N/A | 0.18 | 0 | 0 | 590 | 365 | 1196389 | Original MRA Ccf:0.18; Ccf:0; Pop:590; MTBF:1196389; Cfint:365; OptimumInt: 0 | N | N | N | Y | N | N | N | N | N | N | Substation Crew (2) | 5 | 90 | 40 | 58.33 | 1000 | 3000 | 2000 | -225.5522 | 1 | 0 | 0 | 0 | 0 |  |  | noise
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 10) Provides environmental protection of control cabinet to rating IP53 | a) Does not provide environmental protection of control cabinet to rating IP53 | CONTROL CABINET contaminant ingress due to locking mech failure. (Normal operation). | 171 | Ingress of air and moisture | accelerated degradation of winding and oil. | Check operation of control cabinet door latch. |  | Check operation of control cabinet door latch. |  | TX control cabinet repair. | ZS Inspect |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | N | N | Y | Y | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | peripheral
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 01) Transformation of power from primary to secondary voltage within assigned rating. | b) Does not withstand through fault current. | CORE loss of clamping pressure due to through fault. (Normal operation). | 172 | reduced through fault tolerance | winding failure and loss of supply | Test and record transformer signature using an FRA sweep method. | SFRA | Test and record transformer signature using an FRA sweep method. | Post fault or preassesment for refurbishment | TX repair. | SFRA |  | 120000 | Min Impact / Med Equipment Damage | 0 | 1.1 | 1.1 | 0 | 0 | 0 |  | N | N | N | Y | N | N | N | N | Y |  |  | 0 | 0 | 0 | 0 | 0 | 120000 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Winding | major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | N/A | 11) From Earthing analysis | See Earthing analysis | NEUTRAL - EARTH CONNECTION open circuit / high resistance due to corroded termination. (Normal operation). | 188 |  |  | Test and record neutral to earth connection using minimum of 100A ductor is <500 microohms. Examine neutral connection for correct size and signs of damage. | Micro Ohm | Test and record neutral to earth connection using minimum of 100A ductor is <500 microohms. Examine neutral connection for correct size and signs of damage. | See Earthing analysis. | TX neutral connection repair / replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Earthing | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | WINDING insulation failure due to degradation of paper (Furans Test). (Normal operation). | 174 | Possible failure of transformer. | To be updated | Test transformer oil sample for dissolved gases using main tank oil sample. | Oil Sample | Test the transformer oil sample from main tank valve for dissolved gases. | If DGA results indicate overheating or any partial discharge/arcing, perform a "Degree of Polymerisation Test" on a sample of the cellulose insulation of the transformer and assess. | TX oil replacement with filtered oil. # TX replace. # TX oil sample required. | 1yr DGA Oil Sample |  | 120000 | Min Impact / Med Equipment Damage | 0 | 0.3 | 0 | 770 | 0 | 936833 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | N | N | N | Y |  | Substation Crew (2) | 30 | 90 | 550 | 660 | 0 | 120000 | 0 | 3325 | 1 | 770 | 140525 | 600000 | 2 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | WINDING insulation failure due to electrical damage (Gassing/Arcing). (Normal operation). | 178 | Possible failure of transformer. | To be updated | Test transformer oil sample for dissolved gases using main tank oil sample. | Oil Sample | Test the transformer oil sample from main tank valve for dissolved gases. | Test more frequently once oil has failed an test parameter. | TX oil replacement with filtered oil. # TX oil sample required. | 1yr DGA Oil Sample |  | 120000 | Min Impact / Med Equipment Damage | 1.45 | 0.1 | 0 | 770 | 3650 | 181323 | CF is an estimate on how long we have left them after failing this test.. Original MRA Ccf:100; Ccf:0.1; Pop:500; MTBF:1823.177; Cfint:3650; OptimumInt: 0 | N | Y | Y | Y | N | N | N | N | Y |  | Substation Crew (2) | 10 | 90 | 55 | 91.67 | 60000 | 980000 | 800000 | 538 | 1 | 211 | 32090 | 60000 | 2.4 | Winding | Major
TX 01 01 01 | ZS Power Transformer | Zone and Subtrans. Generic Transformers. | TX010101 Zone and Subtrans. Generic Transformers. | Essential Energy | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | WINDING insulation failure due to degradation of paper. (Normal operation). | 184 | Possible failure of transformer. | To be updated | Test and record DDF (Dielectric Dissipation Factor) of transformer winding. Tan Delta to be less than 10 milliwatts per var (1%) with no step change in capacitance. | DDF | Test and record DDF (Dielectric Dissipation Factor) of transformer winding. Tan Delta to be less than 0.01 watts per var (1%) with no step change in capacitance. |  | TX Insulation testing required. # TX replace. | 6yr Maint. |  | 120000 | Min Impact / Med Equipment Damage | 0 | 0.3 | 0 | 770 | 0 | 936833 | Original MRA Ccf:0; Ccf:0; Pop:0; MTBF:0; Cfint:0; OptimumInt: 0 | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 20 | 90 | 120 | 660 | 600000 | 740000 | 20000 | 3325 | 1 | 770 | 140525 | 600000 | 2 | Winding | Major
TX 01 01 01 | ZS Power Transformer | cool | TX010101 Zone and Subtrans. Generic Transformers. | N/A | 02) Provides insulation of live equipment. | a) Does not provide insulation of live equipment. | WINDING insulation failure due to degradation of paper. (Normal operation). | 185 |  |  | Test the 10 minute / 1 polarisation index of transformer is > 2.0 | IR | Test the 10 minute / 1 polarisation index of transformer is > 2.0 |  | TX oil replacement with filtered oil. # TX replace. | 6yr Maint. |  | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 |  | N | Y | Y | Y | N | Y |  |  |  |  | Substation Crew (2) | 0 | 0 | 0 | 0 | 20000 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Winding | Major

## Sheet2
Operation Loss | Cond Fail: | Funct Fail: | Total Fail: | Pop'n: | CF Interval | MTBF | Examination Time (m): | Exam Success | Setup Cost | Exam Cost | Planned Repair Cost | Call Out, Secondary Damage | Unplanned Failure Cost | Optimal Interval | Protective systems | Protective Population | Protective MTBF | Protective Repair | Protective Failures | C_i | C_p | C_u | R_t | 1 - R_t | MTBF | Optimum
120000 | 6.6 | 0.1 | 0 | 770 | 3650 | 41948 | 15 | 98 | 55 | 110 | 40000 | 960000 | 800000 | 268 | 1 | 210 | 11614 | 40000 | 6.6 | 165 | 40000 | 1760000 | 0.98507 | 0.014925 | 41948 | 1.5655
filter_cols = ['Failure Cause', 'Proposed Task', 'Test', 'Scheduled Task', 'Scheduled Interval', 'Asset Consequence Model', "Level Consequence Model"] df_tasks = df_fmeca[filter_cols] df_tasks.head()
filter_cols = ["Operation Loss:","CF Interval", "MTBF", "Examination Time (m):", "Exam Success", "Setup Cost", "Exam Cost", "Planned Repair Cost", "Call Out, Secondary Damage", "Unplanned Failure Cost"] df_params = df_fmeca[filter_cols]
def optimum_interval(operation_loss, cf_interval, mtbf, exam_time, exam_success, setup_cost, exam_cost, planned_repair_cost, call_out, unplanned_failure_cost): inspect_cost = exam_cost * exam_time + setup_cost # Inpsection Cost penalty = operation_loss + call_out # Penalty T = cf_interval inspect_success = exam_success optimum = math.log(((-mtbf / T) * inspect_cost) / (penalty * math.log(1 - inspect_success))) / math.log(1 - inspect_success) optimim_interval = T / optimum return optimum_interval