## Inputs
Cause |  |  | Failures | [6 empty] | condition |  |  |  | inspection strategy |  |  |  |  | PM |  |  |  |  | CM
component | issue | reason | failure_model | alpha | beta | gamma | pf_curve | pf_interval | pf_std | condition | dist | perfect | failed | inspect_interval | unit | inspect_threshold | inspect_p_effective | inspect_cost | trigger | condition | threshold_max | threshold_min | action | trigger | condition | threshold_max | threshold_min
pole | broken | termites | pbt | 50 | 1.5 | 10 |  |  |  | wall_thickness | pf_linear | 100 | 0 | 5 | years | 95 | 80% | 100 | on_condition | wall_thickness | 95 | 50 | Termite_ | on_condition | safety_factor | 50 | 10
[10 empty] | external_diameter | pf_linear | 100 | 0

## Model Input
| asset_model |  |  | indicator_model |  |  |  | failure_model | [6 empty] | condition_model | [5 empty] | task_model | [13 empty] | trigger_model | [7 empty] | impact_model
| system | sub_system | component | indicator |  |  |  | failure_mode | distribution | [5 empty] | condition | [5 empty] | task | [6 empty] | time |  |  | task_group | apportion_costs |  |  | state |  |  |  |  | condition |  |  | state |  |  | condition
id | name | name | name | name | pf_curve | perfect | failed | name | alpha | beta | gamma | pf_curve | pf_interval | pf_std | name | pf_curve | pf_interval | pf_std | perfect | failed | name | p_effective | cost | trigger | task | activity | level_of_repair | t_delay | t_interval | Level of Failure | task_group_name | admin | maint | travel | initiation | detection | failure | has_strut | value? | name | lower | upper | initiation | detection | failure | name | target | method | axis
|  |  | pole | wall_thickness | linear | 125 | 0 | termites | 50 | 1.5 | 10 | linear | 8 | 1 | external_diameter | [5 empty] | inspection | 0.8 | 50 | time | inspection | Inspection | as_bad_as_old | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE |  |  |  |  | wall_thickness | 0 | -20 |  | TRUE
|  |  |  | external_diameter | linear | 250 | 0 | [7 empty] | wall_thickness | [24 empty] | external_diameter | 0 | -10
|  |  |  | simple_safety_factor | ssf_calc | 4 | 1
|  |  |  | actual_safety_factor | dsf_calc | 6 | 1 | [13 empty] | termite_powder | 0.9 | 100 | condition | repair | ConditionTask | grp |  |  | fm |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 50 | max | FALSE | FALSE | FALSE | all | 0 | reduction_factor | condition
|  |  |  | lightning_damage | step | TRUE | FALSE | [32 empty] | external_diameter | 50 | max
|  |  |  | fire_damage | step | TRUE | FALSE
|  |  |  | impact_damage | step | TRUE | FALSE | [13 empty] | CAT3/4 replacement | 1 | 3500 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
|  |  |  | lean_angle | step | TRUE | FALSE | [32 empty] | external_diameter | 0 | 50
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[8 empty] | fungal decay - external | 50 | 2.9 | 20 | linear | 10 | 1 | external_diameter | [5 empty] | inspection | 0.8 | 50 | time | inspection | Inspection |  | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE
[21 empty] | CAT3/4 replacement | 1 | 3500 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[40 empty] | external_diameter | 0 | 50
[40 empty] | safety_factor | 0 | 3
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[8 empty] | fungal decay - internal | 10 | 3 | 20 | linear | 10 | 1 | wall_thickness | [5 empty] | inspection | 0.8 | 50 | time | inspection | Inspection | as_bad_as_old | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE
[21 empty] | pole_saver_rod | 0.9 | 100 | condition | repair | ConditionTask | as_bad_as_old | [7 empty] | TRUE | TRUE | FALSE |  |  | wall_thickness | 50 | max | FALSE | FALSE | FALSE
[40 empty] | external_diameter | 50 | max
[21 empty] | CAT3/4 replacement | 1 | 3500 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[40 empty] | external_diameter | 0 | 50
[40 empty] | safety_factor | 0 | 3
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[8 empty] | lightning | 50 | 1.5 | 10 | linear | 20 | 1 | lightning_damage | [5 empty] | inspection | 0.99 | 0 | time | inspection | Inspection | as_bad_as_old |  |  |  | assisted_failures |  |  |  | TRUE |  |  |  |  | lightning damage | TRUE | TRUE
[21 empty] | inspection | 1 | 50 | time | inspection | Inspection |  | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE |  |  |  |  | lightning damage | TRUE | TRUE
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[8 empty] | fire_damage | 50 | 1.5 | 10 | linear | 20 | 1 | external_diameter | [5 empty] | inspection | 1 | 0 | time | inspection | Inspection | as_bad_as_old |  |  |  | assisted_failures |  |  |  | TRUE |  |  |  |  | fire_damage | TRUE | TRUE | FALSE | FALSE | FALSE
fire_damage
[21 empty] | CAT3/4 replacement | 1 | 3500 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[40 empty] | external_diameter | 0 | 50
[40 empty] | safety_factor | 0 | 3
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[8 empty] | impact | 50 | 1.5 | 10 | linear | 20 | 1 | impact_damage | [5 empty] | inspection | 1 | 0 | time | inspection | Inspection | as_bad_as_old |  |  |  | assisted_failures |  |  |  | TRUE |  |  |  |  | external_diameter | 0 | 50 | FALSE | FALSE | FALSE
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[8 empty] | weathering | 50 | 1.5 | 10 | linear | 20 | 1 | wall_thickness | [5 empty] | inspection | 1 | 0 | time | inspection | Inspection |  |  |  |  | level_3_inspection |  |  |  | TRUE |  |  |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE
external_diameter
[21 empty] | CAT3/4 replacement | 1 | 3500 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[40 empty] | external_diameter | 0 | 50
[40 empty] | safety_factor | 0 | 3
[21 empty] | CAT1/2 replacement | 1 | 7000 | condition | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
|  |  | pole footing | leaning | step | FALSE | TRUE | any reason | 50 | 1.5 | 10 | linear | 20 | 1 | lean_angle | [5 empty] | inspection | 0.8 | 50 | time | inspection | Inspection | as_bad_as_old | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE | [8 empty] | TRUE
[21 empty] | CAT3/4 replacement | 1 | 100 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[40 empty] | external_diameter | 0 | 50
[40 empty] | safety_factor | 0 | 3
[21 empty] | CAT1/2 replacement | 1 | 200 | detection | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
|  |  | pole_cap | missing | step | FALSE | TRUE | any reason | 50 | 1.5 | 10 | linear | 20 | 1 | external_diameter | [5 empty] | inspection | 0.8 | 50 | time | inspection | Inspection | as_bad_as_old | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE | [8 empty] | TRUE
wall_thickness
[21 empty] | Pole cap replacement | 1 | 100 | condition | replace | ConditionTask | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[40 empty] | external_diameter | 0 | 50
[40 empty] | safety_factor | 0 | 3
[21 empty] | Pole replacement | 1 | 200 | detection | replace | ConditionTask | as_good_as_new |  |  | component | [6 empty] | TRUE | [5 empty] | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
|  |  | crossarm | cross_sectional_area |  |  |  | Fix_this_error | 10 | 10 | 10 | linear | 10 | 10 | add_no_condition_method | [5 empty] | strut | 0.9 | 50 | condition | modify | ConditionTask |  |  |  | component | strut | no | no | no | TRUE | TRUE | FALSE | FALSE |  | wall_thickness | 50 | max |  |  |  | wall_thickness | 50 | addition
|  |  |  | crack_length | [35 empty] | external_diameter | 170 | max |  |  |  | external_diameter | 50 | addition
Note on G5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 125
Note on AO5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 20mm of wallthickness loss not detectable
Note on G6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 250 mm
Note on AO8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm with Peter Couch / Greg Toms
Note on AO13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: add safety factor back
Note on V44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Peter Couch Reply: probs delete
Note on D56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Change task type to planned / reactive / risk?
Note on D62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How do we deal with failures that accelerate other failure modes?
Note on I62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Break it out later
Note on AB62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How do you want to deal with inspections that also include some of repair, ie. lubrication? Add an additional task?
Note on V64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Make this a repair task
Note on D70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How do we deal with failures that accelerate other failure modes?
Note on AB70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: How do you want to deal with inspections that also include some of repair, ie. lubrication? Add an additional task?
Note on V72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Make this a repair task
Note on E78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: fix method to allow multiple indicators for one component
Note on I78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Create error catch for this method

## Asset Heirarchy
|  |  |  | System | Sub System | Module | Maintainable Item
System | Component | Material | Treatment
| Pole |  |  | Pole
| Pole Stay |  |  |  | pole
| Pole Cap |  |  |  |  | pole
| Pole Footing | [5 empty] | pole (common)
pole (timber)
pole (concrete)
pole (steel)
pole (composite)
pole footing
pole footing
pole fixtures
attachments
pole cap
steps
pole stay
pole attachment
top attachment point
thimble
thimble
wire
dead end
wire
insulator
batten
sight guard
anchor rod
anchor rod
footing
pole modification
reinforcement
nail
strut
acroprop
pole accessories
fauna protection
fauna protection
stay protection
cattle guard post

## Failure Modes
Failures | [6 empty] | Indicators
failure_model | alpha | beta | gamma | pf_curve | pf_interval | pf_std | Condition
[pole] {broken} due to (termites) | 50 | 1.5 | 10 | linear | 20 | 1 | external_diameter
|  |  |  | linear | 20 | 1 | wall_thickness
[pole] {broken} due to (lightning) |  |  |  | step | 1 | 1 | nil
[pole] {broken} due to (impact) | 50 | 1.5 | 10 | step |  |  | nil
[pole] {broken} due to (fire damage) |  |  |  | step |  |  | external_diameter
[pole] {broken} due to (fungal decay - internal) | 80 | 2 | 5 | linear | 10 | 1 | wall_thickness
[pole] {broken} due to (fungal decay - external) |  |  |  | linear |  |  | external_diameter
[pole] {broken} due to (weathering) |  |  |  | linear |  |  | external_diameter
[pole foundation] due to (unknown)
[pole cap] due to (unknown) | 1000 | 1.15 | 0 | linear | 20 | 1 | pole_cap_present
[pole stay] due to (unknown) |  |  |  |  | 25
[pole stay] due to (impact)
[pole stay] due to (corrosion)
[pole stay] due to (bed log)
[pole top equipment] due to {cracking} | 50 | 1.5 | 10 | step |  |  | cracking_present
[pole top equipment] due to {cracking} | 50 | 1.5 | 10 | step |  |  | cracking_present

## Indicators
Component | Indicators | dist | perfect | failed
Pole | wall_thickness | pf_linear |  | 0
| external_diameter | pf_linear |  | 0
| simple_safety_factor | sf | 4 | 1 | ssf
| actual_safety_factor | dsf_calc |  | 1 | asf
Footing | nil
Stay | nil
Pole cap | pole_cap_present | step
| top_of_pole_stregnth |  | 100 | 20

## Tasks
[15 empty] | Trigger | [7 empty] | impact
|  | tasks | [5 empty] | time |  |  | task_group | apportion_costs |  |  | state |  |  |  |  | condition |  |  | state |  |  | Condition
component | failure_mode | task_name | p_effective | cost | trigger | task | level_of_repair | t_delay | t_interval | Level of Failure | task_group_name | admin | maint | travel | initiation | detection | failure | has_strut | value? | condition_name | threshold_min | threshold_max | initiation | detection | failure | condition_name | target | method | axis
pole | termite | inspection | 0.8 | 50 | time | inspection | as_bad_as_old | 20 | 5 | nil | level_3_inspection | yes | no | yes | TRUE | any | any
|  | termite_powder | 0.9 | 100 | detection | repair | grp |  |  | fm |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 50 | max | FALSE | FALSE | FALSE
[20 empty] | external_diameter | 50 | max | FALSE | FALSE | FALSE
|  | replacement | 1 | 3500 | detection | replace | as_good_as_new |  |  | component |  |  |  |  | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE | all | 1 | reduction_factor | condition
[20 empty] | external_diameter | 0 | 50
[20 empty] | safety_factor | 0 | 3
pole | fungal decay | inspection | 0.8 | 50 | schedule | inspection |  | 20 | 5 |  | level_3_inspection | yes | no | yes | TRUE | any | any |  |  | nil | nil | nil | nil | nil | nil | nil | nil | nil | nil
|  | pole_saver_rod | 0.9 | 100 | state | repair | [8 empty] | TRUE | TRUE | FALSE |  |  | wall_thickness | 50 | max | FALSE | FALSE | FALSE | nil | nil | nil | nil
[20 empty] | external_diameter | 50 | max | FALSE | FALSE | FALSE
|  | early_replacement | 1 | 3500 | condition | replace | [8 empty] | TRUE | TRUE | FALSE |  |  | wall_thickness | 0 | 50 | FALSE | FALSE | FALSE
[20 empty] | external_diameter | 0 | 50
[20 empty] | safety_factor | 0 | 3
|  | emergency_replacement | 1 | 7000 | condition | replace | [8 empty] | any | any | TRUE |  |  | nil | nil | nil | nil | nil | nil
|  | strut | 0.9 | 50 | condition | modify |  |  |  | component | strut | no | no | no | TRUE | TRUE | FALSE | FALSE |  | wall_thickness | 50 | max | nil | nil | nil | wall_thickness | 50 | addition
[20 empty] | external_diameter | 170 | max | nil | nil | nil | external_diameter | 50 | addition

## CostModel
Component | Failure Mode | Task | rul_min | rul_max | cost | dist | pf_std
Pole | [pole] {broken} due to (termites) | inspection | min | max | 50
|  | termite_powder | min | max
|  | replacement | 0 | 1 | 100000 | fixed
|  |  | 1 | 4 | 50000
|  |  | 4 | 52 | 9000
|  |  | 52 | 208 | 7000
|  |  | 208 | max | 3500
Component | Failure Mode | Task | rul_min | rul_max | cost
Pole | [pole] {broken} due to (termites) | inspection | min | max | 50 |  | weeks
|  | termite_powder | min | max | 36
|  | CAT1/2 replacement | 0 | 26 | 30000
|  | CAT3/4 replacement | 26 | max | 7000

## DELETE
Cause
component | issue |  | reason
[pole] | {broken} | #REF! | (vandalism)
[pole] | {broken} | #REF! | (lightning)
[pole] | {broken} | #REF! | (impact)
[pole] | {broken} | #REF! | (fire damage - bushfire)
[pole] | {broken} | #REF! | (fire damage - asset related)
[pole] | {broken} | #REF! | (extreme environment)
[pole] | {broken} | #REF! | (fungal decay - brown rot)
[pole] | {broken} | #REF! | (fungal decay - carroty rot)
[pole] | {broken} | #REF! | (fungal decay - white rot)
[pole] | {broken} | #REF! | (termites)
[pole] | {broken} | #REF! | (fungal decay - external soft rot)
[pole] | {broken} | #REF! | (weathering)
[pole] | {cracked} | #REF! | (weathering)
[pole sapwood] | {insecure} | #REF! | (weathering)
[pole sapwood] | {insecure} | #REF! | (termites)
[pole] | {degraded appearance} | #REF! | (vandalism)
#REF!
#REF!
[pole foundation] | {eroded} | #REF! | (wear)
[pole foundation] | {eroded} | #REF! | (extreme environment)
[pole foundation] | {eroded} | #REF! | (environment)
[pole foundation] | {loose} | #REF! | (any reason)
[pole foundation] | {ruptured} | #REF! | (impact)
#REF!
[pole cap] | {missing} | #REF! | (installation error)
[pole cap] | {loose} | #REF! | (any reason)
[pole cap] | {falls out} | #REF! | (any reason)
[step] | {missing} | #REF! | (any reason)
[step] | {loose} | #REF! | (weathering)
[attachments] | {too low} | #REF! | (installation error)
#REF!
[label] | {missing} | #REF! | (any reason)
[label] | {not observable} | #REF! | (age)
[label] | {not observable} | #REF! | (out of specification)
[tag] | {missing} | #REF! | (any reason)
[tag] | {not observable} | #REF! | (age)
#REF!
#REF!
[top attachment point] | {loose} | #REF! | (any reason)
#REF!
[thimble] | {missing} | #REF! | (any reason)
[thimble] | {loose} | #REF! | (misalignment)
[dead end] | {broken} | #REF! | (corrosion)
[dead end] | {broken} | #REF! | (fatigue)
[dead end] | {loose} | #REF! | (installation error)
[wire] | {broken} | #REF! | (corrosion)
[wire] | {broken} | #REF! | (overloaded)
[wire] | {broken} | #REF! | (fatigue)
[wire] | {broken} | #REF! | (impact)
[wire] | {broken} | #REF! | (lightning)
[insulator] | {broken} | #REF! | (lightning)
[insulator] | {broken} | #REF! | (impact)
[insulator] | {broken} | #REF! | (environment)
[insulator] | {missing} | #REF! | (installation error)
[sight guard] | {broken} | #REF! | (impact)
[sight guard] | {missing} | #REF! | (installation error)
#REF!
[anchor rod] | {broken} | #REF! | (corrosion)
[anchor rod] | {broken} | #REF! | (impact)
[footing] | {eroded} | #REF! | (wear)
[footing] | {eroded} | #REF! | (extreme environment)
[footing] | {eroded} | #REF! | (environment)
[footing] | {loose} | #REF! | (any reason)
#REF!
#REF!
[nail] | {broken} | #REF! | (overloaded)
[bands] | {broken} | #REF! | (overloaded)
[bands] | {loose} | #REF! | (installation error)

## brainstorming
Inputs |  |  |  |  | Outputs
Asset |  |  |  |  | Probability of Failure
Operational | [12 empty] | Pole Sre
Environment
Health
[14 empty] | Trigger |  | Impact |  | Level of Impact
[5 empty] | Questions for Occa | [8 empty] | Time |  | nil |  | Nil
[5 empty] | Condition v Symptom | [8 empty] | Condition |  | as-bad-as-old |  | FailureMode
[5 empty] | Modifier v Acceleration Factor |  |  |  | Fungal Decay species |  |  |  |  | State |  | better_than_old_worse_than_new |  | Component
[5 empty] | Simple -> Modifier -> Af -> Physics of Failure | [10 empty] | as_good_as_new |  | Parent
[5 empty] | How to include failure mode initiation? | [8 empty] | Schedule |  | new
Indicator
An asset that has made it 100 years?
Degrade condition
|  |  | failure mode | component | [7 empty] | inspection | repair | restore | replace |  | impact | reduction_factor
Task | [8 empty] | trigger | [7 empty] | nil | nil
| Trigger | [8 empty] | time | [6 empty] | as-bad-as-old | 0
|  | Time | [7 empty] | state | [6 empty] | better_than_old_worse_than_new | 0.5
|  | State | initiated |  |  | State |  |  |  |  | initiated | [5 empty] | as_good_as_new | 1
|  |  | detected | [7 empty] | detected | [5 empty] | new | 1
|  |  | failed | [7 empty] | failed
|  | Indicator |  | Condition | [5 empty] | condition
|  | Time |  | Safety Factor |  |  |  |  | impact
time
state
condition
indicators
Asset Data |  |  |  |  | Material | Treatment | Condition | Age
|  |  |  | Asset Model | 4 | 4 | 3 | 10 | 480 | 60 | 28800
8
Greg -> Life extension
life extension
| Multiple tasks are triggered |  |  | replace
reinforce
termite powder
| impact | change an indicator
Calibration scenario
Strength | 4 | kN
ED | 250 | mm
Length | 12.5 | m

## Sheet3
Story to explain
[9 empty] | SSF | PLP SF
| inspection interval for new poles |  | SSF | PLP SF |  |  | Inputs | Pole Strength | WASP | WASP
| inspection interval for each poles | Pole Strength | 14 | 14 |  |  |  | Pole Load | pole_strength/4 | PLP
|  | Load | 3.5 | 1.75 |  |  |  | AGD | WASP | WASP
[8 empty] | CZD | WASP | WASP
|  | AGD | 320 |  |  |  |  | WT | WASP | WASP
For each type |  | CZD | 100
|  | WT | 10
Starting Condition
| Age |  | 3.7 | 7.4
|  |  |  | pole_strength / pole load | pole_load = pole_ strength / 4
pole_strength / actual load
WASP